Content of the Tech-Check Lists is based on several sources incl

tech-check architectural  I core & shell complex

This is a template, so some items will apply to your project, and others won’t or will be missing.

When using the list, make the changes needed for your project.

uding MASTERSPEC®.

| ## ◻ | ## reference documents - DIMENSIONING - CHECK the “Dimensioning Guidelines - Architectural Projects”. - OTHER CHECK LISTS – “Building Code” and “Accessibility.” - NOTATION HELP – “Drawing Notation,” “General Notes for Core & Shell.” - Coordinate abbreviations with list in Cover Sheet. |
| --- | --- |
| ## ◻ | ## TITLE BLOCK - Project name and Address. - Owner’s legal name and address. (check with Google) - Issue Number, Description (Issue for Bid, Addendum A, etc.) and date of issue. - Additional information such as general contractor, when known and approved by Principal. - Initials in “Drawn By” and “Checked By”; plot date. - Stamp. - Scale, Project Number. - Drawing Title / Drawing Number. - Deltas for Addenda and subsequent Bulletins when applicable. |
| ## ◻ | ## Always do this: - Number SIMILAR components for clear notation: Glass #1, Glass #2; Storefront #1, Storefront #2, etc. Note the designations in the Schedule of Finishes and other schedules and refer to the components by its designation throughout the set. - Check that the designations in the schedules match the designations on the drawings. - Always talk to reps. Confirm capacities, sizes, configuration, availability, use. Send your plans for reviewing when applicable. - If an item is typical and you know it, do not add other labels. Add UON only when you know that there is, or probably is, a different condition or materials from the one documented. |
| ## ◻ | ## GRAPHICS - Indicate with dashed lines and label overhead components at building exterior: canopies, awnings, and such. Label them, for example, “CANOPY ABOVE”. - Wall and roof openings: Indicate with an “X” and label “OPEN”. - “North” arrow in every floor plan – oriented in the same way. - Graphic bars (these are required by some agencies - check). - Indicate areas in Project Site which are not included in the Contract and label: NIC (“BY OTHERS” can be confusing. Use “NIC” instead.) - Project Site indicated clearly in building plans. |
| ## ◻ | ## Dimensioning - Height dimensions for architectural projects are from top of slab (TOC), top of parapet, top of deck. - Horizontal dimensions for architectural work are to face of structural framing, concrete, and such, except critical dimensions which are to “face of finish”. - First String: Total building dimension (wall-to-wall), closed string. - Second String: Dimensions to structural elements (columns, etc.), closed string. - Next Strings: Components in order of importance; tied to the structure to fix them, opened strings. Critical dimensions (exiting, accommodate equipment, and such) are labeled “CLEAR”. - Generally, do not set dimensioning to less than 1/8”. Go to 1/16” only when you know it can be done in the field or it can be manufactured to that precision level - Refer to RMW Standard Dimensioning Guidelines for Architectural Projects. Check that: - Dimensions in the elevations and sections are indicated in the same format as in the floor plans. - Mayor components are located with a dimension to a column line or edge of slab. - Partitions are located and tagged. - Doors not in a room corner are located by the dimension to the side of the opening. - Openings in horizontal or vertical components are located to “edge of slab” or framing. - Use annotations such as “ALIGN” and “XX eq spaces” instead of numerical dimensions when applicable. Count carefully! |
| ## ◻ | ## COST MANAGEMENT - Include a summary of alternates and allowances where it is easily found and read. - Alternates - Base Bid work is clearly described throughout the set, including in the Schedules and specifications (book or sheet). - Alternate work is clearly described, including installation when applicable. - The cost of alternate work is calculated by the contractor, and given to the Owner to decide if the alternate work proceeds or not. - ALLOWANCES - Allowance work is clearly described with drawings or in writing or both. - Allowance type is indicated as Unit Price (cost per area o per unit) or as a Fixed Sum. - The allowance amount is fixed by the Owner and the contractor confirms if the allowance is enough. |
| ## ◻ | ## Consistency - Terminology is the same throughout. - Components are tagged with the same tag throughout the set. - Work which is the same has the same tab. - Address only the contractor, no one else, as if he was in front of you: “Do this”, “Do that”. - Graphics representing the same item or work are consistent: Size, type, etc., (for example, finishes, types of partitions, and such). |
| ## ◻ | ## Mockups - If you want mockups, list them and coordinate with the specifier. - Indicate on the Drawings where do you want the mockups (location and extent), when applicable. |
| ## ◻ | ## NO-NOs - Do not describe building envelope finishes and other elevation information in the floor plans. - Do not use periods in the abbreviations: (UON not U.O.N). - DO NOT INCLUDE RATED ASSEMBLIES THAT DO NOT HAVE A UL NUMBER (or other number by any other testing agency). NEVER DESIGN YOUR OWN RATED ASSEMBLIES! - DO NOT use the UON all the time, use ONLY WHEN NEEDED. When you use UON you are telling the contractor that somewhere in the documents there is or there might be a condition which is different to the one with the UON tag, so the contractor has to search all the documents for it, so unless this is the case, drop the UON. |

1 GENERAL

| ## ◻ | ## COORDINATION WITH THE SET - Coordinate abbreviations used in the set with list in Cover Sheet |
| --- | --- |
| ## ◻ | ## CHECK THAT THIS IS INCLUDED: - Abbreviations - General notes – check that they are applicable to the project. - Project name and address. - Title 24 notes. - Drawing List. - Project Directory. - Vicinity Map. - Project Information and code data. - Separate permits and deferred submittals. - Project Legend - Graphic symbols used on the project. |
| ## ◻ | ## REQUIREMENTS - Code Analysis and calculations - Calculations (Exiting requirements) and if applicable, fixture requirements. - CALGreen Checklist - Separate Sheet - ADA/ Accessibility Path of Travel Layouts - Accessibility Standard Details (maneuvering clearances, signage, etc.) - Compliance Statements if required by the local Authority Having Jurisdiction |
| ## ◻ | ## ACCESSIBILITY - Accessibility Standard Details (maneuvering clearances, signage, etc.) - Door and wall accessible toilet signs as applicable to the Project. - Exit signage - Route and stairs when applicable - REFERENCE ONLY: - Accessibility clearances in bathroom floors. - Showers accessibility clearances. - Enlarged bathrooms or toilet plans showing accessibility clearances. |
| ## ◻ | ## SIGNAGE - Door and wall accessible toilet signs as applicable to the Project. - Exit signage - Exit route and stairs when applicable. |

2 COVER SHEET and FRONT-END SHEETS

| ## ◻ | ## IMPORTANT! - In this tech-check list it is assumed that site plans are included only to document path of travel. If the project work includes other than minor modifications to the path of travel or to other sitework, use the list for “BASIC CORE&SHELL” list to check site plans. - For projects where parking is in the building where the work will be done, include the building parking plan to document path or travel. |
| --- | --- |
| ## ◻ | ## PLANS SHOW THESE existing conditions (AS APPLICABLE) - Building footprint, main access, secondary access. - Ramps, curb ramps, sidewalks/walkways, steps or stairs: Locations and configurations. - Signage. - Stripping. |
| ## ◻ | ## MINOR WORK IF INCLUDED - Re-stripping. - New sign - Adding or remodeling access ramps. |
| ## ◻ | ## TAG Existing conditions as applicable - Access to site from point of connection to public road. - Access roads, driveways, turn-arounds, including with and slope. - Location of entrance signage. - Driveways, access, exiting. - Pedestrian traffic. - Accessible path of travel. - Accessible parking signage. - Stripping. - Accessible Details - Site Entry Sign. |

3 SITE PLAN(S). FOR PROJECTS WHERE SITE WORK IS NOT INCLUDED

| ## ◻ | ## Coordination with consultants - Soils report: Read recommendations on soil work, waterproofing, etc. - Building footprint. - Property lines and easements. - Site topography (grading). - Ramps, curb ramps, sidewalks/ walkways, steps or stairs: Locations and configurations. - Parking layout and sloping. - Trees and planting areas. - Utilities. - Exterior lighting. - Signage. - Areas for Contractor’s use – IF determined by Owner. - Landscape areas are indicated with footage if required by AHJ. - Utility lines or service points of connection. |
| --- | --- |
| ## ◻ | Coordination with existing conditions - AS APPLICABLE - Building footprint, main access, secondary access. - Ramps, curb ramps, sidewalks/walkways, steps or stairs: Locations and configurations. - Signage. - Stripping.. - Access to site from point of connection to public road. - Access roads, driveways, turn-arounds, including with and slope. - Location of entrance signage. - Driveways, access, exiting. - Pedestrian traffic. - Accessible path of travel. - Accessible parking signage. - Stripping. - Accessible Details - Site Entry Sign. |
| ## ◻ | ## coordination within the set - Where Plans are subdivided into segments due to size or configuration, insert a “KEY PLAN” with “Match Lines” that show the segments (numbered) and where they are in the Set. |
| ## ◻ | ## SITE INFORMATION: ## (WHEN POSSIBLE obtain a list of what should be shown in the site plan from the local jurisdiction.) - Parcel number. - Access to site from point of connection to public road. - Access roads, driveways, turn-arounds, including with and slope. - Property lines: - Distance between buildings and property lines. - Required fire rating in selected portions of the building due to distance from property lines. - Easements, dimensioned, located in plan, and labeled (utilities, right-of-way, etc.) - Setbacks. |
| ## ◻ | ## SITE CONSTRUCTION - Trash enclosure, elevations, plans, and details. Check if the trash enclosures are required to have a roof and drains. (Trash enclosures do not have doors, they have gates). - Bicycle lockers and racks. - Accessibility details: Signage, and tactile surfacing. - Accessible parking stalls plans. - Access ramps and pipe railings. - Location of entrance signage. - Fences and gates located in reference to property lines when applicable. - References to details are coordinated. |
| ## ◻ | ## PARKING: - Driveways, access, exiting. - Pedestrian traffic. - Parking layout, number of slots, dimensions, flow of traffic, signage. - Accessible path of travel. - Parking signage. - Parking appurtenances. - Fire hydrants if required by permitting agency. |

4 SITE PLAN(S). FOR PROJECTS WHERE SITE WORK IS INCLUDED

| ## ◻ | ## Coordination within the set, AS APPLICABLE - The following key references are indicated and correctly labeled: - Building elevations - show arrow perpendicular to elevation (“go around” the building to check) Tag elevations by location (North, South,Southeast) - Building sections - end arrows pointing the right way. - References to building sections. - References to details are coordinated. - Exterior stairs are indicated and tagged. - Dock pit is indicated and tagged showing extent of excavated area. |
| --- | --- |
| ## ◻ | ## COORDINATION WITH the PROJECT TEAM - Coordinate with electrical engineer for locations of electrical service to architectural components, including lighting, motor operated doors, motor operated dock equipment, etc. - Location of floor, ceiling, and wall mounted electrical components. - Coordinate dimensions of roof openings with the structural engineer. - Coordinate dimensions of chase walls with mechanical / plumbing engineers, if already part of the Project team, particularly where Plumbing fixtures are back-to-back rows of water closets. - Coordinate location of light fixtures, outlets, equipment or furnishings that require power, etc.. - Coordinate location of light fixtures and controls with furnishings. |
| ## ◻ | ## Graphic information and sheet notation - North Arrow in all floor plans in the same direction. - NIC areas clearly marked by shading or any other graphic way. - Move notes and Information describing items located in walls, partitions, and ceilings to Elevations and RCPs sheets. - Sheet Notes and Key Notes: - Review notes to check they all apply to the project. - Notes that address the same thing should be repeated exactly (copy-paste) and if possible with the same number throughout. If a note is not used in a sheet, leave the number and write “NOT USED”. - Check that the terminology is the same as the terminology on the drawings (tags, schedules and notes). BASICALLY CALL THE SAME THING THE SAME WAY THROUGHOUT. - Indicate overhead components at building exterior (awnings, roof components, etc) with dash-lines and label, for example: “CANOPY ABOVE”. - Indicate with an “X” and label floor openings “OPEN”. - Indicate overhead components at building exterior (awnings, roof components, etc) with dash-lines and label, for example: “CANOPY ABOVE”. - Indicate with an “X” and label floor openings “OPEN”. DIMENSIONING - Dimensions in architectural drawings are from structural element (columns, face of concrete, etc.), face of framing (studs, etc.) or face of sheathing (plywood, - Order of dimension strings: - First String: Total building dimension (wall-to-wall), closed string. - Second String: Dimensions to structural elements (columns, etc.), closed string. - Next Strings: Components in order of importance; tied to the structure to fix them, open strings. - Critical dimensions (exiting, accommodate equipment, and such) are labeled “CLEAR”. Dimensions in the elevations and sections are indicated in the same format as in the floor plans. |
| ## ◻ | ## NO-NOs - Do not DESCRIBE building exterior finishes and other elevation information in the floor plans. |
| ## ◻ | ## Partitions - Partition types selected do not exceed the maximum height indicated in the partition details. If you have questions on this, call Gloria or Josie. - Partitions are tagged one by one or in group (note “PARTITION TYPE A UON”). - Plumbing and mechanical chase walls are coordinated with the consultants for wall depths required to accommodate piping or ducts, particularly where plumbing fixtures are back-to-back rows of water closets. - Fire ratings at partitions and doors at electrical and IT/computer server have been coordinated with the electrical engineer. - Chase walls selected are: - Correct for the fire-ratings required. - Their purpose has been checked with the mechanical / plumbing consultants. - Widths is enough to accommodate what is scheduled to be carried (piping, ducts, etc.) - Fire rated partitions are correct for the fire ratings required. - At rated partitions with wall reveals an additional layer of gypsum has been added to maintain the fire rating. - Depths required by fully-recessed or semi-recessed items, such as fire extinguisher cabinets and toilet accessories, are adequate. |
| ## ◻ | ## FLOOR finishes - Starting point for tiling work is indicated. - An enlarged plan is included if necessary to clearly indicate floor finish layout. - Details for floor finishes transitions are tagged. |
| ## ◻ | ## DOORS - All doors tagged; tag doors only in the floor plans, not in the enlarged plans. - Door numbers correspond to the room numbers. - Doors in rooms with multiple doors are tagged sequentially, for example, doors in Room 1001 are tagged as 1001A, 1001B, 1001C, etc. - Sidelights are tagged as one unit along with the adjacent door, not separately. - Door tags are coordinated with the Door & Frame Schedule and the Hardware Groups. - Door sidelights and vision panels are labeled as “SAFETY GLAZING”. - Required clearances at doorways (doors and gates) are correct and labeled. - Direction of door swing meets code. ## Exterior doors - Tagged correctly in the following categories: Hollow Metal (no “man doors”, overhead coiling doors (motor operated or manually operated), or sectional doors. |
| ## ◻ | ## EXITING WIDTHS - Required minimum clear exiting widths at stairs, hallways and corridors are provided or exceeded and labeled as “CLEAR”. - Aisles with cabinets that open towards the aisle (in the full-open position) do not reduce the required minimum clear exiting width. |
| ## ◻ | ## Fire extinguishers - Travel distances to nearest fire extinguisher are indicated (max. 75’). - Cabinet types are labeled: Rated or non-rated, recessed; semi-recessed; surface-mounted. - Partition type widths are sufficient to accommodate recessed and semi-recessed cabinets. - References to drawing and detail number that show accessible mounting heights for cabinets are included. |
| ## ◻ | ## DOCKS - Location of dock bumpers - Location (footprint) of dock leveler (if motor operated coordinate with electrical consultant). |

5 FLOOR PLANS

| ## ◻ | ## COORDINATION WITH THE DESIGN TEAM - Items such as motors, projection screens and overhead coiling grilles or coiling doors concealed in the ceiling space do not conflict with Structural or MEP (if there are included in the Project team) elements and that required clearances are provided. - Location of electrical and mechanical items. |
| --- | --- |
| ## ◻ | ## CEILINGS - Schedule: Products including tiles or panels and suspension system. - “Heavy Duty” type for all. - Areas without ceilings are marked ‘NO CEILING’ or ‘OPEN TO STRUCTURE ABOVE’. - Location of overhead equipment or other items is coordinated. - Layout does not include tiles or panels smaller than ½ a unit or are cut in a way they cannot be suspended. - Extent of each new ceiling is shown. - Ceiling and Soffit heights indicated; 9’-0” AFF, UON. - Light fixtures - Layout of ceiling grids. - Ceiling-mounted items, such as screens, air supply diffusers, return air grilles, exit signs, operable partitions, overhead doors, etc. |
| ## ◻ | ## COORDINATION WITH FF&E: - Access to items such as light switches, outlets, thermostats, access panels, electrical panels and similar items are not blocked by fixed furniture. |

6 REFLECTED CEILING PLANS

| ## ◻ | ## COORDINATION WITH THE DESIGN TEAM - Location of furniture. - Location of floor, ceiling, and wall mounted electrical components. |
| --- | --- |

7 POWER AND COMMUNICATION PLANS

| ## ◻ | ## FINISH SCHEDULE TEMPLATES ARE AT THE END OF THIS DOCUMENT - References to floor plans are the correct. - References in elevations to details are correct. |
| --- | --- |
| ## ◻ | ## COORDINATION WITH the PRODUCT REPS - Finishes are correct for intended use. - Finishes are available and ready for sale. - If needed, extra materials for replacements or patching are available. - Warranties are available. - Installation is easy. - Maintenance is easy. |
| ## ◻ | ## DRAWINGS - Locations and extent of finishes are clearly indicated and finishes are tagged and scheduled. - Finish products are described correctly. |

8 FINISH PLANS

| ## ◻ | ## Coordination within the set - The following key references are indicated and correctly labeled: - Details. - Enlarged plans. - Type of roofing assembly has been confirmed with the specifier and the roofing manufacturer representative. - Details shown correspond to the applicable roof type. - Roof dimensions are shown. - References to building sections. - References to details. |
| --- | --- |
| ## ◻ | ## Terms - Roof Membrane: Single Ply (TPO or PVC) - Board insulation. - Protection board if under the roofing membrane; cover board if over the roofing membrane |
| ## ◻ | ## ROOF CONSTRUCTION - Heights are to top of concrete, steel deck, or parapet - Parapets. - Perimeter drainage. - High and low points of the roof. - Slope directions and slope ratios. Cricketing. - Roof drains and overflow drains - Mechanical/ Electrical/ Plumbing units (future location - dashed - if not in the contract) - Roof equipment screens. - Maintenance pads. - Guardrails and fall protection rails when required. - Roof Access: Hatches and ladders. - Expansion Joints. - Seismic Joints. - Walking pads. - Stairs over equipment. - Skylights. - Window washing equipment. - Ladders at roof perimeter. |

9 ROOF PLAN

| ## ◻ | ## NO-NOs - Do not indicate building envelope finishes and other elevation information in the floor plans. - DO NOT describe materials in the elevation notations, just identify them (GL1, GL2, etc.) UNLESS IT IS NECESSARY FOR CLARITY. Describe materials in the Exterior Finishes Schedule. |
| --- | --- |
| ## ◻ | ## An example of a schedule of exterior finishes is at the end of this document. |
| ## ◻ | ## COORDINATION WITH THE DESIGN TEAM - Structural components. - Exterior levels. |
| ## ◻ | ## DIMENSIONING - Horizontal Dimensions: - First dimension: Exterior wall to exterior wall – match floor plans. - Second dimension: Column lines. - Vertical Dimensions: - Heights: To top of sheathing, top of concrete, top of parapet, top of equipment screen. - Heights of canopies, and other appurtenance. - Openings: To face of opening (framing or concrete) except if critical (dimension only to locate if the item in the opening if the item dimensions are indicated in a schedule, such as doors, windows, etc. |
| ## ◻ | ## INDICATE: - Sections at least in two directions. - Gridlines. - If possible, indicate items in the front plane with one line weight and items in the back planes with a lighter line weight. - Materials tagged on all sides of the building by type (for example, GL1, GL2, and included as such in the Exterior Finish Schedule. - One section for every type of exterior wall arranged in the sheet in order. - Materials tagged. - References to details coordinated. - Door elevations and types are coordinated with the door schedule. |
| ## ◻ | ## aluminum glazed assemblies - Tagged correctly in the following categories: - Storefront: From top of slab to underside of floor deck above not to exceed 14 feet high. - Curtain wall: From top of slab to underside of floor or roof deck above, 14 feet or two floors or more high. - Ribbon walls: Running continuously constructed with storefront components. - Punched Walls: Single openings in the building envelope. - Glass types identified and tagged. |

10 BUILDING ELEVATIONS

| ## ◻ | ## COORDINATION WITH THE DESIGN TEAM - Structural components. - Exterior levels. |
| --- | --- |
| ## ◻ | - Sections at least in two directions. - Grid lines. - One section for every type of exterior wall arranged in the sheet in order. - Grid lines. - Heights to top of parapet and top of sheathing, building clear height, and top of openings. - Materials tagged. - References to details. |

11 BUILDING SECTIONS

| ## ◻ | ## Before you enlarge a plan, make sure it is necessary! |
| --- | --- |
| ## ◻ | ## Coordination within the set - References to floor plans are the correct. - References in elevations to details are correct. |
| ## ◻ | ## ITEMS INDICATED - Locations and extent of finishes are clearly indicated and finishes are tagged and scheduled. - Elevation is complete and enclosed: Floor, ceiling (show changes in ceiling and floor levels if applicable), side walls or end of walls. - Openings are crossed and labeled “OPEN”. - Heights are indicated as AFF. - Room doors and cabinet doors show swing. - Elevations of the same room are together. |
| ## ◻ | ## Showers and janitor rooms - Showers: - Elevations: Show fixtures, bench, shelf for shampoo, soap dish, hook, and curtain/rod. - Plans: Indicate curb at non-accessible showers, - Partitions on Wet Side: Backboard (not gypsum) on wet side, tile over mortar over waterproofing. - Shower Receptacle: Waterproofing unde pre-manufactured receptacle (preferred). - Janitor Rooms: - Elevations: Show shelf for cleaning stuff and protective panels to waist height. - Plans: Show janitor floor sink. |

12 ENLARGED PLANS

| ## ◻ | ## Coordination within the set - References to floor plans are the correct. - References in elevations to details are correct. |
| --- | --- |
| ## ◻ | ## Showers and janitor rooms - Showers: - Elevations: Show fixtures, bench, shelf for shampoo, soap dish, hook, and curtain/rod. - Plans: Indicate curb at non-accessible showers, - Partitions on Wet Side: Backboard (not gypsum) on wet side, tile over mortar over waterproofing. - Shower Receptacle: Waterproofing under pre-manufactured receptacle and extending to the room (preferred). - Janitor Rooms: - Elevations: Show shelf for cleaning stuff and protective panels to waist height. - Plans: Show janitor floor sink. |

13 Interior ELEVATIONS

| ## ◻ | ## COORDINATION IN THE SHEET - As much as possible keep details of the same family together. - Check that in details that include the same assembly, the assembly is the same (size of door frames, type of floor slab, etc. - Check that items in the details are tagged in the same manner (overhead deck is always overhead deck”, “window” is always “window”, etc. |
| --- | --- |
| ## ◻ | ## GRAPHICS - Details are grouped by families. - Graphic representation of items is consistent. - Terminology is consistent and correct. |

14 building details - GENERAL

| ## ◻ | ## ARCHITECTURAL CONCRETE - Locations and the extent of cast-in-place architectural concrete. Distinguish from structural concrete or concrete not to be considered as cast-in-place architectural concrete. - Details clearly defining sizes, shapes, and dimensions of cast-in-place architectural concrete sections. - Details of special formed patterns and textures. - Location and the extent of each type of exposed architectural concrete finish. - Locations and patterns of exposed form tie holes. Include the diameter of tie cone. - Locations, the extent, and finishes of associated formed surfaces not requiring cast-in-place architectural concrete finishes. - Locations and details of chamfers. - Locations and details of contraction and construction joints. - Locations and details of inserts, built-in frames, openings, and items where work of other trades will be attached to or supported by formwork. - Locations of mockups. |
| --- | --- |
| ## ◻ | ## Polished concrete - Extent of polished concrete floors. Extent of each type and color of stain if any. Locations of decorative scoring if any. - Locations, and size of mockups. |
| ## ◻ | ## PRECAST ARCHITECTURAL CONCRETE Basis of Design Manufacturer: Clark Pacific. - Layout of the framing system. Show the relative location of various precast concrete units, floor elevations, openings, column centers and offsets, and dimensions. - Locations and types of finishes. Include thin brick and stone facings. - Details of connections and joints. Show anchorage devices, other embedded items, and grouting. - Details of openings. - Fire-resistance-rated construction and joint-filling requirements. |
| ## ◻ | ## Cmu Basis of Design Manufacturer: Basalite. - Extent of each type and thickness of concrete unit masonry. - Extent of each fire-resistance rating if any, and identification of fire-resistance design designation or equivalent thickness. - Location and detail of each type of movement joint. Show isolation joints between masonry and concrete and between masonry and steel framing if any. S - Locations, types, and details of items, such as anchors, ties, inserts, lintels, flashings, and reglets, to be built into masonry. - Details of special masonry features, such as chases, recesses, and openings for other work, if known. - Joint thickness and coursing heights if critical. - Joint profiles if other-than-specified concave tooling. - Pattern bonds for exposed surfaces if other-than-specified running bond. |
| ## ◻ | ## MASONRY VENEER - Extent of each type of masonry product (masonry units, mortars, accessory items). Use the same terminology used in the Section Text. - Location and detail of each type of movement joint. - Locations, types, and details of items such as flashings. - Details of openings. - Joint thickness and coursing heights if critical. - Joint profiles if other-than-specified concave tooling. - Colored mortar if any. Indicate whether colored-aggregate mortar or pigmented mortar. - Pattern bonds for exposed surfaces if other-than-specified running bond. - Extent of each type of masonry accessory item (anchors, flashing, etc.) if more than one type of the same item is required. |

15 details - Concrete and masonry

| ## ◻ | ## ARCHITECTURALLY EXPOSED STRUCTURAL STEEL FRAMING - Locations of structural-steel items considered to be architecturally exposed structural steel; coordinate with the structural Drawings. - Location of the mockup, if any. - Sheet Note: Welds to be ground smooth. |
| --- | --- |
| ## ◻ | ## COLD-FORMED METAL FRAMING (load-bearing stud framing) Basis of Design Manufacturers: Clark Dietrich and Cemco. - This item is always either “delegated design” or calculated and designed by the structural engineer. - Extent of each form of load bearing cold-formed metal framing. - Identification of exterior and interior load-bearing walls from exterior and interior non-load- bearing walls. - Depth, thickness, shape, height, finish, and spacing of each component, but only to the extent not specified. - Details at abutting construction. - Locations and construction details of control joints and building expansion joints. - Special framing, blocking, and bracing to support fixtures and other work from the framing system. - Extra studs or other reinforcement at doors and other significant openings. |
| ## ◻ | ## Metal fabrications - Extent of each fabricated item. Include plans, elevations, and details as applicable. - Name of each item. Coordinate with Specification terminology. - Metal types and finishes if more than one. Coordinate with Specification terminology. - Metal thicknesses and other dimensional data not specified, or exceptions to default sizes. - Profiles and details. Include cutouts, returns, reveals, edge finishing, stiffeners, jointing, and anchoring. - Concealed flashings, if required to make exterior construction weathertight. |
| ## ◻ | ## PIPE AND TUBE RAILINGS (interior or exterior) - Locations and the extent of railings with adequately dimensioned plans and details. Show guard infill design to the extent it is not specified. - Material sizes and types. - Finishes: Galvanized for exteriors, primed for interiors. Location of each metal finish if more than one. - Locations of removable railing sections, if any. - Railing details at bends and returns, handrail bracket design and connections, and connections of railings to building structure. - Infil panels type. |
| ## ◻ | ## DECORATIVE METAL RAILINGS - Locations and extent of railings, dimensioned and detailed. - Material sizes and types. - Location of each metal and finish if more than one. - Locations of removable units if any. - Details of guard construction and spacing of elements. - Anchorage and connection details. - Species and profiles of wood handrails if not specified. - Locations of expansion joints if any. - Railing details at bends and returns, handrail bracket design and connections, and connections of railings to building structure. - Lengths or the number of fluorescent tubes for illuminated decorative railings if any. Indicate circuiting of illuminated railings on electrical Drawings. |
| ## ◻ | ## DECORATIVE GLASS RAILINGS - Locations and extent of railings, dimensioned and detailed. - Material sizes and types. Coordinate terminology with the Specifications. - Location of type of glazing and each metal and finish if more than one. - Glass is either fully tempered or laminated (both are “safety glazing”). - Anchorage and connection details. - Glazing details. - Railing details at bends and returns, handrail bracket design and connections, and connections of railings to building structure. - Lengths or the number of fluorescent tubes for illuminated decorative railings if any. Indicate circuiting of illuminated railings on electrical Drawings. |

16 dETAILS - METALS and railings

| ## ◻ | ## LADDERS - DO NOT detail ladders: Ladders have strict OSHA requirements so are pre-manufactured. O'Keeffe's. Is the basis of design product. Choose a ladder model - call for recommendations if unsure - and insert cut sheet in the drawings. http://okeeffes.com/ |
| --- | --- |
| ## ◻ | CODE COMPLIANCE - Landing and adjacent doors: Accessibility clearance. - Plan, elevations, and sections: Widths. - Projections on the width. - Headroom clearances. - Tread size and configuration. - Handrails configuration and heights. - Handrails extensions at top and bottom of stairs. - Space under stairs is open. |
| ## ◻ | ## Metal pan stairs (these are our standard pre-manufactured fire stairs) Basis of Design Manufacturer: American Stair. - Extent of metal pan stairs. Include plans, elevations, and details. Indicate types of metal pan stairs if more than one type. - Extent of railings. Include plans, elevations, and details. If railings are included with preassembled stairs and railing configuration is specified in this Section, do not show details that limit the manufacturer's construction methods unnecessarily. - Profiles of treads and risers. - Types of treads and landings if more than one type. - Types of nosings. Include profiles and dimensions. - Finishes: Primed for field painting for interiors; galvanized for exteriors. - Supporting construction and methods of attachment. - Elements of fire-resistive construction enclosing the stairs. |
| ## ◻ | ## METAL GRATING STAIRS (THESE ARE OUR STANDARD PRE-MANUFACTURED UTILITARIAN STAIRS) Basis of Design Manufacturer: American Stair. - Extent of metal grating stairs. Include plans, elevations, and details. Indicate types of metal grating stairs if more than one type. - Extent of railings. Include plans, elevations, and details. - Profiles of treads and risers. - Types of treads and landings if more than one type. - Types of nosings. Include profiles and dimensions. - Finishes: Primed for field painting for interiors; galvanized for exteriors. - Supporting construction and methods of attachment. |

17 dETAILS - LADDERS AND STAIRS

| ## ◻ | ## Coordination within the set - Extent of miscellaneous carpentry. Include section sizes. - Details of typical and special conditions. - Blocking: Indicate continuous (two diagonals at section) or not (one diagonal at section). - Locations where pressure-preservative-treated and fire-retardant-treated wood are required. |
| --- | --- |
| ## ◻ | ## Sheathing - Extent of each type of panel product. In our projects we typically use plywood sheathing and gypsum sheathing. - Thickness of each type of panel product. - Extent of wood structural panels required to be plywood. - Locations where pressure-preservative-treated and fire-retardant-treated plywood are required. |
| ## ◻ | ## Miscellaneous carpentry - Extent of each type of exterior finish carpentry. - Details of construction and relationship with adjacent materials, including flashing, sealants, vapor retarders, building wraps or air barriers, and insulation. - Profiles of trim, moldings. - Extent of preservative-treated finish carpentry. - Species and grades of lumber if not fully covered by the Specifications. - Furring and blocking needed for installing other work. |

18 details - CARPENTRY (for architectural woodwork see interiors list)

| ## ◻ | ## Bentonite waterproofing (this is our standard waterproofing product) Basis of Design Product: Bentonite by Tremco (sheet-applied). - Locations and details of bentonite waterproofing. - Connections to or coordination with flashings, expansion joints, waterstops, transitions to other types of waterproofing, and other elements of the substrate and waterproofing systems. - Locations and details of protection-course applications if any. - Locations and details of subsoil drainage systems. - Unusual provisions recommended by the manufacturer. - Insulation coordination details if any. |
| --- | --- |
| ## ◻ | ## TRAFFIC COATINGS Basis of Design Manufacturer: Dex-O-Tex. - Locations and extent of traffic coatings for each type. - Details at deck-to-wall and deck-to-curb terminations. - Details and flashings at drains and other waterways. - Details of coating terminations at the edges of expansion and seismic joints. - Details of preparation, treatment, joint sealants, and bond breaking at substrate joints and cracks. - Details to control upward hydrostatic pressure of slabs-on-grade that receive traffic coatings, such as a vapor barrier and drainage aggregate. - Layout of pavement markings. |
| ## ◻ | ## Sheet air barriers (product below is fire tested as part of an assembly and can be used in rain screens) Basis of Design Product: ExoAir® 110 by Tremco. - Locations and extent of air barriers - sections showing building envelope assemblies. - Materials to bridge and seal exterior wall air-leakage pathways and gaps, including the following: - Connections of walls to foundations. - Seismic and expansion joints - Openings. - Penetrations. - All other air-leakage pathways in building envelope. |

19 details - water and air intrusion protection

| ## ◻ | ## Formed metal WALL PANELS - Extent of metal panels and other accessories or components. - Profiles of metal panels. - Details of metal panel edges and seams. - Details of trim and other accessories. Include profiles and dimensions unless the manufacturer's standard units are acceptable. - Details of flashings, door and window openings, louvers, penetrations, and panel interfaces with roofs, soffits, and expansion joints. - Fire-resistance ratings, and similar code and safety requirements, testing agency, testing agency design number, and other requirements to the extent required by authorities having jurisdiction. - Specific metal panel support and anchorage systems. Show sizes, shapes, locations, spacings, and methods of attaching girts, angles, channels, and other structural supports and anchors. - Gaskets and sealants at joints, if required, and special separation of metals if not sufficiently specified or covered by the manufacturer's standard details (particularly specific locations). - Location of each metal panel color if more than one is required. - Aluminum finishes (anodized or two-coat fluoropolymer - three coats if metallic) DO NOT use “PAINTED” as tag. - Steel finishes: Galvanized or “factory-applied manufacturer’s standard finish”. DO NOT use “PAINTED” as tag. - Locations of mockups if required. |
| --- | --- |
| ## ◻ | ## Column covers - If possible, use same manufacturer as aluminum panels. - Location and extent of each column cover, dimensioned and detailed. - Profiles and details of column covers. Include cutouts, returns, reveals, edge finishing, stiffeners, jointing, and anchoring. - Aluminum finishes (“anodized” or ”fluoropolymer.”) DO NOT use “PAINTED”as tag. - Details of anchorage to adjacent construction. |
| ## ◻ | ## METAL COMPOSITE MATERIAL WALL PANELS - Extent of metal panels and other accessories or components. - Details of trim and other accessories. I - Details of flashings, door and window openings, louvers, penetrations, parapets, and panel interfaces with roofs, soffits, and expansion joints. - Fire-resistance ratings, testing agency, testing agency design number, and other requirements to extent required by authorities having jurisdiction. - Specific metal panel anchorage and support assemblies. Show sizes, shapes, locations, spacings, and methods of attaching metal plate support assembly and sub-framing including girts, angles, channels, and other structural supports and anchors. - Gaskets and sealants at joints, if required. - Location of each metal panel color if more than one is required. - Locations, views, and details of mockups if required. |

20 details - building envelope - metal panels

| ## ◻ | ## ROOF - Parapet showing coping and transition to roof. - Roof drain. - Downspout - Skylight, plan and section at curb. - Scooper at roof, including scupper box and flashing box. - Roof hatches - show post and railings. - Equipment screen. - Penthouses. |
| --- | --- |
| ## ◻ | ## POLYVINYL-CHLORIDE (PVC) ROOFING AND THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING Basis of Design Product: PVC or TPO 60 mils roofing by Johns Manville - Roof plan indicating extent of each type of roofing. Include slopes, drain locations, tapered insulation locations and slopes, and sheet roofing termination conditions. - Rating (Underwriters Laboratories or other testing agency) and the testing agency's design designation for roof areas requiring fire-resistance ratings. - Board insulation: thicknesses, number of layers, and taper of insulation if required. Show locations and extent of crickets. - Flashing, nailers, and reglets at terminations of roofing. Show nailers if required. - Remodeling and Additions: Tie-ins with other roofing systems, both existing and new. - Locations and details for sheet metal accessories. Include the metal type if several types are specified. Show the relationship of membrane roofing to metal flashings. - Locations and large-scale details of roof expansion joints; area dividers; hatches, skylights, and other accessories; equipment supports. - Details of preformed, vent-pipe flashings. - Details of roof drains and scuppers. - Locations and dimensions of walkway products. - Widow washing equipment. - Roof equipment screen. - Access ladders where needed on roof, and at roof at to access penthouses roofs. - Assemblies: - INSULATED - Over composite deck: Board insulation / Protection board / Roof membrane - INSULATED - Over steel deck: Base board / Board Insulation / Roof membrane - NOT INSULATED - Over composite deck: Base board / Roof membrane - NOT INSULATED - Over steel deck: Base board / Roof membrane |
| ## ◻ | ## ROOF ACCESSORIES - Location, size, and configuration of each roof accessory. - Flashing and cant details of roof accessories. Show cricket details where accessory obstructs the flow of water toward a drain. - Details of each roof accessory. Include profiles and interfaces with other work and security grilles if required at roof curbs. Indicate extent of security grilles if only some units require them. - Coordination of each roof hatch with its roof opening, the access stair or ladder, the space between steps, and toe clearances. Verify roof hatch opening location and orientation with respect to fall-prevention requirements. - Coordination of roof walkway locations with access and servicing points for roof-mounted equipment. - Height of roof curbs and equipment and pipe supports above the roof's surface. Coordinate this height with space needed for roof maintenance and replacement. - Configuration and details of roof-hatch safety railing. - Anchorage details. Include provisions for deck reinforcement at openings. - Special framing to accommodate multiple units. - Material, finish, and color designations if not uniform for all units of any type of roof accessory. specified. Indicate surfaces to receive field-applied paint. - Location and attachments for window washing equipment. |
| ## ◻ | ## VEGETATED ROOF SYSTEMS - The best approach for vegetated roofs, whether at roof or balconies, is for RMW to design the entire system, including the planters, and leave to the landscape consultant only the soil selection and planting. Coordinate depth of planters with plants selected. - Coordinate weight of roof with structural engineer. - Extent and details of each type of vegetated roof assembly installation. Coordinate depth of continuous assembly and tray depth and tray size of tray-type assembly with manufacturers. - Extent and details of related roofing and accessories, including roof slope, and roof assembly. Coordinate with vegetated roof assembly. - Locations and details of pavers and their installation. Coordinate heigh and installation of pavers with planters. - Locations and details of access boxes, and other accessories. - Thickness and finish grades of growing medium that suit plant root systems, surface drainage, and desired visual effect. - Curb heights for skylights and other rooftop elements. Coordinate with roof slope and thickness of vegetated roof assembly, including growing medium. - Location and details of roof expansion-joint assembly. Coordinate with vegetated roof assembly. - Locations of hose bibs. - Coordinate with landscape consultant: - Layout of drainage and irrigation systems. - Layouts, arrangements, and spacing of plantings. Identify plants by species and size. - Obstructions such as overhead clearances, rooftop piping, equipment, and ductwork that may affect installation of vegetated roof assembly. - Electrical connections for electronic leak-detection system if required in the roofing system. |

21 details - ROOF

| ## ◻ | ## APPLIED FIREPROOFING - Locations and extent of fireproofing. DO NOT indicate thickness unless YOU GET THEM FROM THE MANUFACTURER’S TECHNICAL REPRESENTATIVE. - Schedule or details indicating UL-design designations or designations of another testing and inspecting agency for each assembly if required for permitting. - Locations of restrained beams if designated by the structural engineer. - Finishes (texture and paint) required for fireproofing exposed to view are indicated - this includes exposed under deck fireproofing. COORDINATE WITH FIREPROOFING MANUFACTURER. - Locations and types of auxiliary materials required. - Details of fireproofing assemblies using metal lath and lathing accessories, if any. - Details of construction that encloses or covers fireproofing. Coordinate with fireproofing thickness. - Details of penetrations through fireproofing showing coordination with firestopping. |
| --- | --- |
| ## ◻ | ## INTUMESCENT FIREPROOFING ## MAKE ABSOLUTELY SURE YOU ARE WORKING WITH INTUMESCENT FIREPROOFING AND NOT INTUMESCENT PAINT”. STICK WITH “ALBI” to make sure you have the right product. - Locations and extent of fireproofing. DO NOT indicate thickness unless YOU GET THEM FROM THE MANUFACTURER’S TECHNICAL REPRESENTATIVE. - Finishes required for fireproofing exposed to view are indicated. COORDINATE WITH FIREPROOFING MANUFACTURER. - Schedule or details indicating UL-design designations or designations of another testing and inspecting agency for each assembly if required for permitting. - Locations and types of auxiliary materials required. - Locations and extent of mockups. |
| ## ◻ | ## PENETRATION FIRESTOPPING - this is for penetrations (holes) in rated assemblies - Most of the locations of fireproofing in the project are only known at the time of construction. A few we can identify at the time of documenting the project (for example, electrical boxes in rated partitions) and those are in the Detail library. At the time of construction, a licensed subcontractor will make an inventory of the penetrations and should submit a schedule with the selected assemblies for each case. We only acknowledge that the inventory was made and received by us; we DO NOT REVIEW IT for accuracy or completeness. - If you are adding a detail because of permitting authority requires it, MAKE SURE that the assembly was tested by UL or another testing agency. If you cannot find one, call either TREMCO or HILTI. - NEVER NEVER NEVER design your own firestopping assembly. |
| ## ◻ | ## JOINT FIRESTOPPING - this is for JOINTS in rated assemblies (EDGE OF SLAB, HEAD OF RATED PARTITIONS, FOR EXAMPLE - Locations and fire-resistance ratings of joint firestopping are identified. Coordinate with fire-resistance ratings of constructions in which fire-resistive joints are located. In architectural projects, ALWAYS TALK TO THE MANUFACTURER (TREMCO OR HILTI) and get the appropriate assembly from them. For interior partitions, if the detail is not in the Detail Library, look in the manufacturers website for tested assemblies or call the manufacturer. - DO NOT EVER DESIGN YOUR OWN ASSEMBLY. If the manufacturer hasn’t tested an assembly exactly like yours, they can give you an “engineering judgement”. - Make sure you work with actual joint widths. Coordinate with maximum widths allowed for selected fire-resistive joint systems. - Details of perimeter fire-resistive joint systems. Show relationships to curtain-wall assemblies, spandrels, and adjoining floor assemblies. |

22 details - fire protection

| ## ◻ | ## JOINT SEALANTS - Extent of each type of joint sealant required. Identify the different types of sealants using the terminology in the sealant schedule at the end of the section. - Dimensions and details of typical joint conditions. Include each form of tooled joint configuration, locations where more than one is required, and the location of each if it cannot be described in this Section. - Colors required for each type of joint sealant, if more than one color is required. - Locations for pre-construction and field quality-control adhesion testing. - Coordinate with mockups specified in other Sections that contain joint sealants. |
| --- | --- |
| ## ◻ | ## INTERIOR EXPANSION JOINT COVER ASSEMBLIES - Locations and types of expansion joint cover assemblies. Include adequately dimensioned plans, sections, and details. - Detail of joint corners. - Joint size, movement capability, and the type of movement (thermal, wind sway, or seismic) for each expansion joint. - Three-dimensional illustration showing where expansion joint cover assemblies make transition of planes or change direction, IF REQUIRED FOR CLARITY - Material types. - Types of finish materials to be applied to expansion joint cover assemblies, IF ANY. - Continuity between floor, wall, and ceiling expansion joint cover assemblies. - Locations and fire-resistance ratings of fire-rated expansion joint cover assemblies. Include UL designations. |
| ## ◻ | ## exTERIOR EXPANSION JOINT COVER ASSEMBLIES - Locations and types of expansion joint cover assemblies. Include adequately dimensioned plans, sections, and details. - Detail of joint corners. - Joint size, movement capability, and the type of movement (thermal, wind sway, or seismic) for each expansion joint. - IF REQUIRED FOR CLARITY - Three-dimensional illustration showing where expansion joint cover assemblies make transition of planes or change direction. - Material types. - Types of finish materials to be applied to expansion joint cover assemblies, if any. - Continuity between floor, wall, and ceiling expansion joint cover assemblies. - Locations and fire-resistance ratings of fire-rated expansion joint cover assemblies. Include UL designations. - Drainage of moisture-barrier gutters and connections to plumbing if any. |

23 details - sealants and joint covers

| ## ◻ | ## Coordination within the set - All doors types are tagged and tags are the same throughout. - Coordinate with the Door Schedule, Hardware Groups, and elevations of door types. |
| --- | --- |
| ## ◻ | ## COORDINATE WITH FLOOR PLANS, ELEVATIONS, DOOR SCHEDULE AND DOOR/FRAME ELEVATIONS - Tag of each door opening on plans and in a door and frame schedule. - Hardware group for each door, tag with the door and in the Door Schedule. - Hand of each door and degree of swing. - Size, exposure, special clearances, and so forth, for each door - Special characteristics of doors. Include fire-protection rating, sound rating, and radiation protection requirements. - Special sill, head, joint, lite, louver, or meeting stile conditions affecting type, size, installation, or clearance of door hardware units. - For pairs of doors, location of active leaf. - Special door hardware installation requirements if any. Include unusual security or fasteners, and so forth. - Mounting locations if different from those specified or indicated in referenced standards. - Heights and locations of armor, kick, mop, and stretcher plates. - Locations and details of weather stripping, sound seals, and thresholds. - Coordination of electrified hardware locations with electrical power supply. - Locations of blocking in walls to support wall stops. |
| ## ◻ | ## Hollow metal doors and frames - Locations and elevations of aluminum frames. Clearly delineate between aluminum framing systems and other aluminum framing system applications such as interior aluminum framed doors, and glazed partitions. - Fire ratings for aluminum frames (check ratings availability with manufacturer). - Finish for interiors : Shop primed to be field painted. Note color. - Finish for exteriors: Galvanized to be field painted. Note color. - Glass type(s) and thicknesses if not specified or scheduled. - Anchorage and support system. |
| ## ◻ | ## Aluminum frames - Locations and elevations of aluminum frames. Clearly delineate between aluminum framing systems and other aluminum framing system applications such as interior aluminum framed doors, and glazed partitions. - Fire ratings for fire-rated doors including temperature rise if applicable. - Type, color, and finish if more than one framing profile, color, and finish are required. - Glass type(s) and thicknesses if not specified or scheduled. - Anchorage and support system. |
| ## ◻ | ## Flush wood doors - Location and swing of each door. - Fire ratings for fire-rated doors including temperature rise if applicable. Do not exceed maximum size of vision panels in rated doors. - The following information is indicated the door schedule: - Door mark or number. - Key to door elevation. - Dimensions of door. - Construction of door (typically solid core flush wood door). - Frame material and finish. - Hardware set required. - Threshold type if any. Face materials and finishes. Typically they are: - Core: MDF. - Faces for painted doors (opaque finish): - Faces of veneer doors (transparent finish). Indicate wood veneer species and cut and arrangement of veneers on the door face. - For plastic laminate clad doors indicate plastic-laminate product and colors. - Indicate vision panels on door elevations. - Doors are four sides finished - long sides and faces. If door is visible from above, note five sides finishes including top. |
| ## ◻ | ## ALL GLASS ENTRANCES (FRAMELESS GLASS DOORS) - Locations and extent of all-glass entrance systems. - Type, color, and finish if more than one of each are required. - Glass type and thickness. - Dimensions and configuration requirements of all-glass systems, including swing (hand) or slide directions for all-glass entrance doors. - Patch-,rail-,and accessory-fitting requirements. - Locations and requirements of push-pull and exit devices and other hardware, to the extent not specified. Use a hardware schedule if requirements are not fully specified. - Anchorage and overhead steel support requirements. - Coordination with adjacent construction. |
| ## ◻ | ## SLIDING ALUMINUM-FRAMED GLASS DOORS - Sliding door schedule if the Project requires several sliding door sizes or performance levels. - Extent of each type of sliding door. Show operating- and fixed-panel configurations using conventional symbols (e.g., XO, OX, OX-O, and XO-O, where "X" designates fixed panels and "O" designates operable panels). - Door unit and operable panel sizes. - Details of typical member profiles if critical to the design, or if variations are acceptable, minimum profile requirements. Include support for fenestration combinations. - Height, dimensions, profiles, and details of thresholds. - Hardware if more than one type is required. - Indicate whether interior or exterior doors. |
| ## ◻ | ## OVERHEAD COILING DOORS - Door types, locations, and dimensions. I - Locations of perforations, fenestrations, and vision panels in door slats. - Details of head and jamb conditions and guide mounting. - Door operation method. Indicate chain, crank, or electric motor operator and location of these devices. - Type and location of emergency manual operation. - Clearance dimensions for motors, cranks, chains, and maintenance service. - Mounting details for doors and tracks. - Locations for controls and operators. - Locations and characteristics of electrical power to motors and controls. Coordinate with electrical Drawings. - Fire Rated Doors: Related walls and construction for fire-rated doors must be equal or greater fire resistance than door. |
| ## ◻ | ## SECTIONAL DOORS - Door types, locations, and dimensions. - Locations of windows in door sections and full-vision sections. - Details of head, sill, and jamb conditions and track mounting. - Clearance dimensions for overhead position of the door, motors, counterweights, chain wheels, and maintenance service. - Locations of removable center posts and other options. - Door operation method: Indicate manual push-up, chain, or rope operators or electric motor operators. - Locations for controls and operators. UL 325 requires locating control stations so that the user cannot come in contact with the door while operating the controls. - Locations and characteristics of electrical power to motors and controls. Coordinate with electrical consultant and Drawings. |
| ## ◻ | ## DOOR HARDWARE ## Coordinate with floor plans, elevations, door schedule and door/frame elevations - Tag of each door opening on plans and in a door and frame schedule. - Hardware group for each door, tag with the door and in the Door Schedule. - Hand of each door and degree of swing. - Size, exposure, special clearances, and so forth, for each door - Special characteristics of doors. Include fire-protection rating, sound rating, and radiation protection requirements. - Special sill, head, joint, lite, louver, or meeting stile conditions affecting type, size, installation, or clearance of door hardware units. - For pairs of doors, location of active leaf. - Special door hardware installation requirements if any. Include unusual security or fasteners, and so forth. - Mounting locations if different from those specified or indicated in referenced standards. - Heights and locations of armor, kick, mop, and stretcher plates. - Locations and details of weather stripping, sound seals, and thresholds. - Coordination of electrified hardware locations with electrical power supply. - Locations of blocking in walls to support wall stops. |

24 details - openings - DOORS

| # Table 12-2-1-5 |  |
| --- | --- |
| ## ◻ | ## NOMENCLATURE - STOREFRONT - Ground floor, from top of slab to underside of deck of floor above; maximum 14 feet but check with manufacturer. - CURTAIN WALL - From top of slab if ground floor to underside of roof deck, hanging in front of building with gaps between curtain wall and slab. - GLASS WALL - Same as storefront but in higher floors. - WINDOW - Opening in wall, usually framed with storefront components. - RIBBON WINDOWS: Windows in a row. |
| ## ◻ | ## ALUMINUM-FRAMED ENTRANCES AND STOREFRONTS - Extent of entrance or storefront system. Distinguish between aluminum-framed entrances and storefronts and other aluminum-framed systems, such as windows, curtain walls, and sloped glazing systems; and distinguish between other entrance systems, such as all-glass, automatic, and revolving entrances. - Type, color, and finish if more than one of each are required. - Glass designations. Include safety glazing at entrance systems. - Basic dimensions. - Door elevations. Include rail and stile dimensions, push-pull trim configurations, and hardware mounting heights. - Notation of entrance door hardware sets for each door opening in the door schedule. - Coordination requirements with structural supports, column lines, and floor levels. - Basic anchorage and support systems. - Details of joint sealants and fillers at the interface of entrance and storefront systems and other building components. - Test-area requirements for field testing. |
| ## ◻ | ## ALL-GLASS ENTRANCES AND STOREFRONTS - Locations and extent of all-glass entrance and storefront systems. - Color and finish as required. - Glass designations if more than one type or thickness is required. - Dimensions and configuration requirements of all-glass systems, including swing (hand) or slide directions for all-glass entrance doors. - Patch-, rail-, and accessory-fitting requirements. - Locations and requirements of push-pull and exit devices and other hardware. - Anchorage and overhead-steel-support requirements. - Coordination with adjacent construction. - Test-area requirements for field testing. |
| ## ◻ | ## GLAZED ALUMINUM CURTAIN WALLS - Extent of glazed aluminum curtain walls. Include operable units if any. Distinguish between curtain-wall assemblies and other aluminum-framed systems such as storefront, window, and sloped glazing assemblies. - Type, color, and finish if more than one of each is required. - Glass designations. - Basic dimensions. - Coordination requirements. Include structural support, column lines, and floor levels. - Expansion, deflection, and movement requirements to accommodate building structure and design loads. - Basic anchorage and support systems. - Details of perimeter fire-containment systems (safing insulation). - Details of joint sealants and fillers at the interface of the glazed aluminum curtain wall and other building components. - Connections with adjacent construction, - Integral stabilization requirements for descent-control equipment used for maintenance if any. - Pre-construction laboratory mockup (test specimen) requirements if Project-specific pre-construction testing is required. |
| ## ◻ | ## STRUCTURAL-SEALANT-GLAZED CURTAIN WALLS (these have butt joints) - Extent of structural-sealant-glazed curtain walls. Include operable units if any. Distinguish between curtain-wall assemblies and other aluminum-framed systems such as storefront, window, sloped glazing assemblies, and conventionally glazed curtain walls. - Type, color, and finish if more than one of each is required. - Glass designations. - Basic dimensions. Include glass- and spandrel-panel thicknesses and framing-member profile requirements. - Coordination requirements. Include structural support, column lines, and floor levels. - Expansion, deflection, and movement requirements to accommodate building structure and design loads. - Basic anchorage and support systems. - Connections with adjacent construction, - Details of perimeter fire-containment systems (edge of slab). - Details of joint sealants and fillers at the interface of the structural-sealant-glazed curtain wall and other building components. - Integral stabilization requirements for window washing equipment if any. - Pre-construction laboratory mockup (test specimen) requirements if Project-specific pre-construction testing is required. |

25 details - BUILDING ENVELOPE - ALUMINUM-FRAMED GLAZED ASSEMBLIES

| ## ◻ | ## UNIT SKYLIGHTS - Locations and extent of unit skylights. Coordinate with structural support. - Operating devices, louvers, operable vents, curbs, and flashing integral to unit skylights. - Locations of motors and controls for operating units if any. Coordinate operator wiring requirements and electrical characteristics with the building electrical system. - Rough opening and installation details including curbs, blocking, and framing. Indicate relationship to adjacent construction including flashing, sealants. Include anchorage details. - Details of gutters and flashing for drainage of continuous vaults or clustered-unit assemblies. - Unit skylight schedule. |
| --- | --- |
| ## ◻ | ## METAL-FRAMED SKYLIGHTS - Extent of metal-framed skylights. Distinguish between metal-framed skylights and other aluminum-framed systems such as sloped-glazing systems, curtain walls, and storefronts. - Type, color and finish, and glazing designations if more than one type, color and finish, or glazing material is required. - Basic dimensions. Include glazing panel thicknesses and member profile requirements. - Coordination requirements with structural support. - Coordination requirements with fire protection, temperature-control and air-distribution systems, and lighting and electrical systems. - Details of requirements for smoke evacuation if any. - Details of interface with roof systems. Coordinate with roof slope and roof insulation thickness. Include details of curbs, flashing, and drainage. - Details of joint sealants and fillers at the interface of skylights and other building components. - Details of gutters and flashing for system drainage. - Locations and details of ventilating units, sunshades, opaque panels, and other items installed in skylight framing. For operable items, indicate operators and coordinate electrical requirements. - Test-area requirements for field testing. - Details of code-required screens protecting occupied spaces if any. . |

26 DETAILS - skyLights

| ## ◻ | ## GENERAL Coordinate with floor plans, elevations, door schedule and door/frame elevations, and with glass partitions and windows. |
| --- | --- |
| ## ◻ | ## GLASS - Extent and the location of each different glass product and glazing system. - Detail of joints for butt glazing. - Tags for different types of glazing units. - Dimensions of assemblies. Show framing system or glass opening dimensions rather than actual sizes (width and height) of glass lites. - Complete glazing details. Show glazing channels or rabbets and the kind of glazing method required for each. If wet glazing is specified, indicate the silicone sealant. - Indicate locations of glass with patterns, film, or designs in plans and show layout in interior elevations. |
| ## ◻ | ## MIRRORS - Location of each type of mirror. - Size and shape of each mirror unit; sizes, shapes, and locations of cutouts and notches. - All mirrors are safety glass. - Method of mounting or support. |
| ## ◻ | ## FIRE RESISTANT GLAZING - Extent and location of each different fire-resistant glass product. Tags for each type of product and rating. - Dimensions of assemblies. Show framing system or glass opening dimensions rather than actual sizes (width and height) of glass lites. - Unless Contractor is allowed to use any glazing method approved by testing agencies that listed and labeled fire-resistant glazing products, show complete glazing details. Show glazing channels or rabbets and the kind of glazing method required for each. |

27 details - GLAZING

| ## ◻ | ## STUCCO - Locations and the extent of each type of cement plasterwork required. - Details of exterior cement plaster, weather-resistant barriers installed over sheathing, sealant at V-grooves and other locations, flashing, and methods of draining water that gets behind plaster to the exterior. - Ratings and requirements for fire-resistance-rated assemblies. Include design designations from a qualified testing agency or other means of establishing requirements acceptable to authorities having jurisdiction. - Location of the following: - Insulation, thermal and acoustical. - Control and expansion joints (12 feet horizontally and 12 feet vertically). - Accessories. - Where cement plaster is used as a bed for tile or manufactured stone. - Mockups if any. |
| --- | --- |

28 details - EXTERIOR FINISHES

| ## ◻ | ## STANDARD INTERIOR GYPSUM BOAD PARTITIONS – See Interiors tech-check list. |
| --- | --- |
| ## ◻ | ## SHAFT WALLS - Extent of each gypsum board shaft wall assembly. Tag is the same throughout, - Design designations of a qualified testing agency that has determined the fire-resistance rating of the assembly. - Locations and thicknesses of gypsum board or other finish panels, and the number of layers applied to the room or shaft side of the assembly for each application. - Control joints location or include in sheet note. - Locations requiring sound attenuation blankets or other acoustical treatment. Indicate the location of STC-rated assemblies. - Locations of sprayed fire-resistive materials. Show details of shaft wall assemblies terminating at surfaces protected by sprayed fire-resistive material. - Locations of building structure and other penetrations in gypsum board shaft wall assemblies. - For elevator hoistways, locations of door frames, electrical boxes, elevator call buttons, elevator floor indicators, and similar items. Indicate details of door head and jamb framing. - Locations of fixtures and handrails requiring supplementary framing or blocking. |

29 DETAILS - interior partitions

| ## ◻ | ## HYDRAULIC ELEVATORS - COORDINATE the following with consultants: - Standby power to fused disconnect switches (or circuit breakers) for each elevator that must be able to operate on standby power. Include connections from auxiliary contacts in the transfer switch to elevator controllers. - Dedicated 120-V circuit in the machine room for each elevator controller. - Lighting, switches, and power outlets (120 V) in each machine room and elevator pit. - Fire-detection and -alarm system connections to elevator controllers. - Security-system (access-control) connections to elevator controllers. - Connections for the traveling cable on the electrical and communication Drawings, including the following: - 120-V power supply for car lighting and fan. - Telephone or intercom. - Firefighters' two-way telephone communication service. - Other services as appropriate (e.g., Muzak, security system, and closed-circuit television) - Heating, ventilation, and cooling of machine rooms on HVAC Drawings. Ensure that cooling is provided to maintain an adequate working temperature for microprocessor controls. - Sprinkler coverage of the machine room and shaft on fire sprinkler Drawings if required. NFPA 13 no longer requires sprinklers at the top of noncombustible shafts for passenger elevators that comply with ASME A17.1/CSA B44 and does not require sprinklers at the bottom of noncombustible shafts if combustible hydraulic fluids are not used. ASME A17.1/CSA B44 requires that the power be automatically disconnected to the affected elevator before or on applying water. - Cab finishes: Coordinate with manufacturer’s representative for custom finishes. - Railing at back wall as required ## Finishes of controls in elevator cab and at hoistway walls. |
| --- | --- |

30 details - elevators

| ## ◻ | ## DECORATIVE METAL FENCES AND GATES - Locations of decorative metal fences and gates and their relationship to property lines where relevant. - Locations and types of known underground utilities, landscape irrigation systems, or structures that could interfere with or be damaged by fencing installation. - Plan layout and extent of fence lines, terminal posts, and gates. Indicate decorative metal fence types and locations if more than one type. - Elevation of a typical section of fence. Indicate the spacing of posts and pickets, and the height of posts, rails, pickets, and infill if not specified. Show decorative elements if any. - Diameters and depths of post footings. Show locations of pipe sleeves or voids in concrete for posts, and attachment of fence to other construction. - Gate size. Indicate swing direction and required clearances. For roller gate with bottom wheels show roller track or roller pad. - Locations and identification of gate operating system devices. Indicate concrete base and footing details including reinforcements, mounting details, and required operating clearances for components of gate operating system. - Layout and sensitivity zone or pattern of each loop detection device. - Details of special fencing requirements, such as abrupt changes in grade. - Locations and sizes of electrical grounds and details of methods of electrically isolating long runs of fencing. - Show or note provision of anti-lighting system. |
| --- | --- |
| ## ◻ | ## CHAIN LINK FENCES AND GATES - Locations of chain-link fences and gates and their relationship to structures and property lines. - Coordinate with known underground utilities, landscape irrigation systems, or structures that could interfere with or be damaged by fencing installation. - Plan layout and the extent of fence lines, terminal posts, and gates. Indicate chain-link fence types and locations if more than one type. - Height of chain-link fence fabric. - Line post size, type, and spacing and gate framework components. - Diameters and depths of post footings. Indicate locations of pipe sleeves or voids in concrete for posts, and attachment of fence to other construction. - Locations of rails and tension wires if other than standard top, intermediate, or bottom positions. - Gate and leaf size. Indicate swing direction and required clearances. Show details of electric isolation for gate if any. For roller gates with bottom wheels show roller track installation or roller pad. - Locations and identifications of gate-operating system devices. Indicate equipment base/pad and footing details, including reinforcements, mounting details, and required operating clearances for components of gate-operating system. - Layout and sensitivity zone or pattern of each loop detection device. - Locations of privacy slats and colors. Indicate each type if more than one. - Extent and the arrangement of barbed wire and barbed tape at fence and at gates, if any. - Barbed wire extension arms and the number of wires or coils if not specified. - Location or notes for special fencing requirements, such as anti-lighting devices. |

31 site work

32 EXTERIOR FINISHES SCHEDULE

EXTERIOR FINISHES SCHEDULE SAMPLE

- Materials are grouped by types (all glass types, etc).

- Tags in the elevation are the same as in the Exterior Finishes Schedule.

These are examples to illustrate nomenclature and listing; products named are also examples.

## GLASS - SINGLE PANEL

  - Glass Type:  Clear, fully tempered.

  - Thickness: 1/2 inch

## GLASS - INSULATING

  - Glass Type:

  - Exterior Panel:  1/2” thick, tinted with Low E coating in #2 Surface.

  - Interior Panel:  1/2” thick, clear

  - Interspace:  Air, dehydrated

  - Total Thickness: 1”.

  - Product:  [Solarban 60 by PPG] [insert]

## ALUMINUM FRAMING:

  - Product:  X by Kawneer.

  - Dimensions:  2” by 4-1/2”.

  - Assembly:  Stick.

  - Finish:  [Clear anodized] [insert]

## aluminum composite wall panels

  - Product:  X by Alucobond.

  - Dimensions:  8’ by 4’.

  - Assembly:  Rout & Return.

  - Finish:  [Clear anodized] [insert].

## Formed aluminum wall panels

  - Product:  X by {insert].

  - Dimensions:  8’ by 4’.

  - Assembly:  Rout & Return.

  - Finish:  [Clear anodized] [insert].

## THIN BRICK VENEER (stone similar):

  - Type: Clay Face Brick.

  - Unit Size:  X wide by X height by X long.

  - Product:  X by Basalite, colors [insert].

  - Installation: [thinset over concrete] [mortar bed] [description]GLASS - SINGLE PANEL

## CONCRETE PANELS:

  - Face Up Finish: Troweled.

  - Face Down Finish:  Smooth, as cast.

  - Concrete Coating:  Elastomeric, colors [insert].

  - Product:  [TEX-COTE®] [insert]

## ALUMINUM FRAMING:

  - Product:  X by [Kawneer] [insert]

  - Dimensions:  2” by 4-1/2”.

  - Assembly:  Stick.

  - Finish:  [Clear anodized] [insert]

FORMED METAL ROOF PANELS:  (these panels are fabricated by “folding” metal sheet)

  - Type: Exposed Fasteners.

  - Material:  Galvanized steel sheet.

  - Finishes:  [Manufacturer’s standard] [insert]

  - Product:  [AEP Span, HR-36® Roof & Wall] [Insert]

End of core & shell COMPLEX list